# MYRRHA WCS Engineering Handover — SUMMARY (v0.4)

## Project Overview

Engineering handover bundle for the Warm Compressor Station (WCS) of the MYRRHA cryogenic plant (QPLANT). Compares the two pre-studied warm-compressor concepts — Kaeser FSD 575 SFC (ALaT) vs FSD 475 SFC (LKT) — against a 350 g/s @ 14 barG baseline, sizes utilities, and consolidates the operational envelope under a Greek-letter notation (β / γ / α).

Location: /home/ubuntu/myrrha_handover/ · Entry point: index.html

## Deliverables

### HTML views (13)

| # | File | Purpose |
| --- | --- | --- |
| 1 | index.html | Hub / navigation |
| 2 | slides.html | Interactive deck |
| 3 | slide-editor.html | Dual-view live editor |
| 4 | reports.html | Rendered design arguments B1–B7 |
| 5 | tables.html | Specs · CSV / JSON export |
| 6 | graphs.html | Chart.js plots |
| 7 | status.html | Session TODOs · changelog |
| 8 | truth.html | Immutable design decisions |
| 9 | utilities.html | Math · sample calculations |
| 10 | pvps.html | 2 × 5 LP array · γ = 50 g/s · N+1 |
| 11 | hx-sizing.html | RCW oil cooler · COMBI · Plotly |
| 12 | thermo-analysis.html | Energy / Sankey / T-s / exergy |
| 13 | operations.html | β/γ/α operating windows · 3D surface |
| 14 | handover.html | Agent BIOS · session protocol |

### Master sources (single source of truth)

- master/data.json — all numeric data

- master/slides.md — slide content

- master/truth.md — design decisions

- master/config.yaml — themes / fonts / layout

### Pipeline & docs

- render_all.py, live-render.js

- docs/design-guide.md, docs/editing-guide.md, docs/slide-notes-guide.md

## Key Findings & Recommendations

- Baseline: 350 g/s @ 14 barG holds as the utility-sizing point (β_max).

- Vendor selection: LKT (3 × FSD 475) preferred over ALaT (2 × FSD 575) for finer turndown granularity and N+1 economy.

- PVPS: 2 × 5 LP-unit array (γ_nominal = 50 g/s) provides α = 0.4–1.0 turndown with one-unit redundancy.

- RCW: ΔT 25 °C (30 → 55 °C) on oil pre-cool; HX N+1 strategy pending approval.

- COMBI concept: Fixed 64 Hz + VFD unit promising for Config24 — needs Kaeser confirmation.

- Exergy efficiency: ~44 % (current target); review for v0.5.

## Operational Notation (recap)

- β = WCS.HP flow [g/s], β_max = 350

- γ = PVPS flow [g/s], γ_nominal = 50

- α = γ / γ_max, α ∈ [0.4, 1.0]

- Σ = β + γ (total WCS)

- Design points: Config30 (β=330, Σ=380) · Config24 (β=304, Σ=354)

## Next Steps for Engineering Team

- Critical (blocking): Coldbox QRB interface · COMBI vendor confirmation.

- High: PVPS datasheets · turndown scenarios C30(00,10) / C24(00,10) · RCW HX N+1.

- Medium: Discharge temperatures · noise compliance · waste-heat recovery.

- Low: HVAC allocation · exergy optimization.

## Handover Instructions

- Boot point: open handover.html for agent BIOS and session protocol.

- Edit content: modify files in master/; run render_all.py to regenerate views.

- Versioning: v0.4 = 85 % complete; v0.5 will integrate vendor data + QRB coldbox.

## Contact

Direct continuation in this conversation, or load handover.html § “Next-session boot prompt” into a new agent session.