# MINERVA / MYRRHA P&ID Symbol Library — Legend Analysis

Authoritative symbol reference for the ongoing MINERVA P&ID reconstruction work, extracted from the client/company standard legend sheet.

| Field | Value |
| --- | --- |
| Source document | AD_01.16 SUP - PID General Legend Sheet.pdf |
| Drawing number | 106889-PID00 (P&IDs 106889-PID01, sheets 1–9) |
| Doc number | MYR100PTF-0521 |
| Owner | SCK CEN — MYRRHA / MINERVA project |
| Revision | A (Released), 16/11/2023 |
| Sheet size / count | A1 · 9 legend sheets (10 PDF pages incl. cover) |
| Drawn by / Verified / Approved | Leysen J. / Bergmans G. / Voorderhake S. |

## Standards basis

The legend explicitly subordinates itself to published standards — capture these deviations exactly, because this company legend is the authoritative source and takes precedence over generic ISA-5.1 where they differ:

- ANSI/ISA-5.1-2022 — instrument letter codes (subordinate to Table 4.1) and instrument symbolic representation (subordinate to Table 5.1.1).

- ISO 10628 — process diagram house style (piping / equipment layout).

- IEC 60617 (publication 617) — electrical symbols (Sheet 7). Symbols marked with an asterisk * are non-standard (house additions). Relay function numbers marked ** follow ANSI C37.2.

- Tag numbering — Primary Systems Naming Convention & Terminology SCK CEN/36557490; deviceclass mnemonics SCK CEN/36793249.

## Deliverables (this folder)

| File | Purpose |
| --- | --- |
| legend_symbols.json | Structured catalogue: every symbol + metadata, naming conventions, ISA letter code, bubble matrix, colour/stroke spec, usage notes, and the list of drawn SVG ids. |
| symbol_library.svg | Reusable SVG <defs> of 159 <symbol> elements (zero-size, position:absolute). Reference any symbol with <use href="#<id>"/>. |
| symbol_library_preview.svg / .png | Human-readable contact sheet of every drawn symbol with its id (visual QA). |
| build_legend_library.py | Pure-stdlib generator that (re)produces all of the above. Re-run with python3 build_legend_library.py. |

159 symbols are drawn (schematic, standards-based geometry — not a pixel copy of the CAD source) covering the complete process-P&ID scope of sheets 1–5. The facility-specific (RIB line, beam optics) and electrical/fire sheets (6–9) are catalogued at reference level in reference_only_sets (77 listed items).

## How to use the SVG library

<!-- 1. embed/link symbol_library.svg once (it is defs-only, renders nothing) -->
<!-- 2. place any symbol, scaling freely; each symbol has its own viewBox -->
<svg width="900" height="400">
  <use href="#valve-gate"        x="100" y="100" width="60" height="36"/>
  <use href="#inst-A1"           x="220" y="90"  width="48" height="48"/>
  <use href="#act-diaphragm"     x="320" y="70"  width="70" height="70"/>
  <use href="#line-primary"      x="420" y="110" width="120" height="24"/>
</svg>

All ids are stable, lower-case, hyphen-separated, and namespaced by category prefix (line-, inst-, flow-, valve-, act-, eq-, conn-, iface-, scope-, misc-, hvac-). See svg_library.drawn_ids in the JSON for the full list.

## 1. Line types (Sheet 1)

Line weight is significant and must be honoured:

| Symbol id | Name | Line weight | Style |
| --- | --- | --- | --- |
| line-primary | Primary line segment | 1 mm | solid + arrow |
| line-secondary | Secondary line segment | 0.5 mm | solid + arrow |
| line-primary-future | Primary, future extension | 1 mm | dash-dot + arrow |
| line-secondary-future | Secondary, future extension | 0.5 mm | dash-dot + arrow |
| line-electrical-signal | Electrical signal | 0.25 mm | dashed |
| line-pneumatic-signal | Pneumatic signal | 0.25 mm | double cross-hatch ticks |
| line-hydraulic-signal | Hydraulic signal | 0.25 mm | periodic L-marks |
| line-software-signal | Software / data signal | 0.25 mm | ring markers |
| line-em-sonic-signal | Guided EM / sonic signal | — | wave marker |
| line-capillary | Capillary tube | 0.25 mm | x cross marks |
| line-hose | Hose | — | continuous wavy |
| line-pipe-insulated | Pipe, insulated | — | hatch band |
| line-tracer | Tracer (heating/cooling) | — | parallel dashed trace |
| line-jacketed | Jacketed pipeline | — | outer jacket box |
| line-heated-insulated | Heated/cooled + insulated | — | hatch + trace |
| line-hvac-supply | HVAC air supply | 1 mm | solid |
| line-hvac-return | HVAC air return | 1 mm | dash-dot |
| conn-connected-lines | Connected lines | — | junction bridge |
| conn-non-connected-lines | Non-connected lines | — | hop / gap |

## 2. Instrumentation (Sheet 2 — ISA-5.1 matrix; Sheet 3 — flow elements)

### Bubble matrix (type × location) — inst-<TYPE><ROW>

The legend reproduces ISA-5.1 Table 5.1.1 as a 4-column × 5-row matrix. Type is the enclosure shape; location is the line through the bubble.

Type columns

| Col | Meaning | Shape |
| --- | --- | --- |
| A | Shared display/control — Basic Process Control System (BPCS) | square enclosing a circle |
| B | Shared display/control — Safety Instrumented System (SIS) | square + circle + diagonals |
| C | Computer systems and software | hexagon |
| D | Discrete visualisation of instruments | plain circle (stadium/oval = two instruments → inst-discrete-oval) |

Location rows (accessibility line across the bubble)

| Row | Location | Line |
| --- | --- | --- |
| 1 | Field-mounted; operator accessible | none |
| 2 | Front of central/main panel or console | single solid |
| 3 | Rear of central panel / cabinet behind panel | single dashed |
| 4 | Front of secondary/local panel | double solid |
| 5 | Rear of secondary/local panel / field cabinet | double dashed |

So e.g. inst-A1 = field BPCS bubble, inst-B2 = main-panel SIS, inst-C3 = behind-panel software, inst-D5 = field-cabinet discrete.

### Instrument tag composition (Sheet 1)

Instrument tags are not drawn explicitly; they are composed: 1. take the first line of the tag of the element the instrument is attached to; 2. append the top + bottom parts shown inside the bubble, joined by -.

Example: an LS bubble (LS / 1001) on valve THSITS-GSRSEL:PNE-VALVE-1002 → instrument tag THSITS-GSRSEL:PNE-LS-1001. A TT bubble (TT / 202) on THSITS-GSRSEL:PNE-PIPE-111 → THSITS-GSRSEL:PNE-TT-202.

### ISA letter code (Sheet 2, subordinate to ISA-5.1 Table 4.1)

First letter = measured/initiating variable (+ optional modifier); succeeding letters = readout/passive, output/active, function modifier. The full table is in legend_symbols.json → categories.instrumentation.letter_code. Highlights: F flow, L level, P pressure, T temperature, A analysis, S speed/safety, Z position/SIS; succeeding T transmit, I indicate, C control, R record, S switch, V valve/damper, E sensor/element.

### In-line flow / primary elements (Sheet 3 — INSTRUMENT SYMBOLS)

flow-sonic, flow-variable-area, flow-coriolis, flow-magnetic, flow-vortex, flow-radiation, flow-orifice-generic, flow-nozzle, flow-venturi, flow-positive-displacement, flow-turbine.

## 3. Valves & actuators (Sheet 3)

The base body is the ISA two-triangle bow-tie. Lock/fail state codes are written above the body:

| Code | Meaning | Code | Meaning |
| --- | --- | --- | --- |
| LC | Locked closed | NO | Open in normal operation |
| LO | Locked open | FC | Fail to closed (act-fail-closed) |
| NC | Closed in normal operation | FO | Fail to open (act-fail-open) |
|  |  | FA | Fail as it is (act-fail-as-is) |

Valve bodies: valve-generic, valve-gate, valve-globe, valve-ball, valve-needle, valve-butterfly, valve-angle, valve-three-way, valve-check, valve-swing-check, valve-ball-check, valve-globe-check, valve-tilting-disk-check, valve-piston-lift-check, valve-y-piston-lift-check, valve-butterfly-check, valve-y-globe, valve-safety, valve-safety-spring-angle, valve-pressure-reducing, valve-balancing, valve-differential-pressure.

Actuating elements: act-diaphragm (pneumatic), act-piston, act-hydraulic, act-solenoid, act-manual, act-motor-electric, act-motor-dc, act-motor-pos-transmit, act-self-fcv/pcv/tcv/lcv (self-acting control valves), act-fixed-spring, act-float, act-weight, act-high-speed, act-fail-closed/open/as-is.

## 4. Additional symbols

### Equipment (Sheet 4)

Pumps (eq-pump-liquid, -centrifugal, -cavity), compressors/vacuum (eq-compressor-vacuum, eq-turbo-compressor), eq-blower-fan, heat exchangers (eq-heat-exchanger-general/-u-tube/-plate), eq-electric-heater, eq-steam-generator, eq-chiller, filters (eq-gas-filter, -hepa, eq-liquid-filter, eq-mixed-bed-filter, eq-ion-exchanger, eq-charcoal-filter), tanks (eq-horizontal-tank, -vertical-tank, -conical-tank, eq-hopper), eq-rupture-disc, eq-steam-trap, eq-viewing-glass, eq-orifice-plate-line.

### Connection / end types (Sheet 3)

conn-threaded, conn-flanged-ends, conn-wafer, conn-welded-ends, conn-quick-coupling, conn-hose, conn-flanged-connection, conn-isolating-flange, conn-blind-flange, conn-screw-cap, conn-welded-cap, conn-reducer.

### Interfaces & scope boundaries (Sheet 1)

- iface-termination-point — diamond TPXYYYY / ZZZ. X = interface category: B building, C civil, E electrical, G compressed gasses, H HVAC, L liquid waste, S solid waste, W water; YYYY = unique number; ZZZ = next system/process.

- iface-offpage-connector — XXXXX | 123456-PID01 | WWWWW (unique name | interconnecting P&ID number | from/to process; ZZZZZ = medium).

- iface-system-nfs — interface between (non-primary) systems, e.g. PBS1.

- scope-design-limit — system & design-conditions limit (valve + diamond).

- scope-code-jurisdiction — piping code jurisdiction break (e.g. ASME VIII ↔ ASME B31.3); * denotes the supplier side. Design conditions per code letter are tabulated in boxes on each drawing.

### Miscellaneous / specialty (Sheet 5)

misc-reducer, misc-vfd, misc-flame-arrestor, misc-dielectric-joint, strainers (misc-strainer-y/-t/-cone), misc-sampling-point, misc-atmospheric-vent, misc-spray-nozzle, misc-agitator, misc-compensator, misc-funnel, misc-special-joint.

### HVAC (Sheet 5)

hvac-shutoff-damper, hvac-parallel-damper, hvac-opposed-damper, hvac-fan-general, hvac-radiator, hvac-heating-coil, hvac-cooling-coil, hvac-filter, hvac-supply-terminal, hvac-exhaust-terminal.

## Reference-only sets (Sheets 6–9, not redrawn)

These belong to facility-specific and electrical/fire single-line drawings, outside the core process-P&ID symbol scope. They are listed in legend_symbols.json → reference_only_sets:

- MINERVA RIB line specific elements (Sheet 6) — pillow seal, clamped/thin/ cooled windows, collimator, Hall sensor, magnet, target, bellows, etc.

- MINERVA beam optics (Sheet 6) — beam position/halo/profile/tail monitors, quadrupole, wire scanner, steering plates, Faraday cup, electrostatic bender, mirrors, slits, beam shutter/dump, optical diagnostics, laser/ABU/FCU, etc.

- Electrical symbols (Sheet 7) — IEC 60617; transformers, CTs, breakers, relays, contacts, meters, sounders, etc. (* = non-standard, ** = ANSI C37.2).

- Fire detection / extinguishing / safety (Sheets 8–9) — detectors, sounders, extinguishing controls, fire separations E30/EI30/EI60/EI120, emergency / life-safety pictograms.

## Reconciliation with generator/symbols.py

The hand-built ISA-5.1 primitives in pid_project/generator/symbols.py remain valid but are superseded by this authoritative legend where they differ. Recommended adoption path for the reconstruction:

| symbols.py primitive | Authoritative legend equivalent | Note |
| --- | --- | --- |
| bubble() (plain circle) | inst-D1 (discrete, field) | field discrete instrument |
| bubble_square() | inst-A1 (square + circle) | BPCS shared display |
| dashed bubble (is_safety) | inst-B* (SIS, square+circle+diagonals) | legend uses diagonals for SIS, not a dashed outline — align to inst-B* |
| valve(kind="gate") | valve-gate | bow-tie body matches |
| valve(kind="control") | act-diaphragm | diaphragm-actuated control valve |
| valve(kind="solenoid") | act-solenoid | matches |
| valve(kind="relief") | valve-safety / valve-safety-spring-angle | use angle type for spring-loaded relief |
| vessel() | eq-vertical-tank / eq-horizontal-tank | dished-end vessels |
| heat_exchanger() | eq-heat-exchanger-general | circle + zig-zag |
| terminal_point() | iface-termination-point | legend uses a diamond TPXYYYY/ZZZ, not a crossed circle — switch to diamond |

Key deviations to apply going forward

- SIS instruments use a square+circle with diagonal lines (inst-B*), not a dashed outline.

- Termination points are diamonds carrying TPXYYYY / ZZZ, with the category letter set drawn from {B,C,E,G,H,L,S,W}.

- Line weights are normative: primary = 1 mm, secondary = 0.5 mm, all signal lines = 0.25 mm. Future/proposed lines use dash-dot.

- Off-page continuation uses the arrow-box connector with the interconnecting P&ID number (123456-PID01) and medium.

- Code jurisdiction breaks are explicit symbols (valve + diamond + code letters) and must be placed wherever the piping code changes.

Regenerate everything with: python3 standards/build_legend_library.py