# MINERVA CryoCell P&ID — Colour Scheme Revision Guide (v5)

Project: MINERVA CryoCell — SCK CEN · MYRRHA / MINERVA Phase 1 Consultant: Mott MacDonald (Bristol, UK) · MMD 411066 Status: S2 — FOR ACCEPTANCE · RESTRICTED Standards: SCK CEN AD_01.16 · ISO 10628 · ANSI/ISA-5.1-2022 · IEC 60617

## 1. Purpose of the revision

The v5 revision replaces the legacy colour assignment (which used red for the 40 K shield and treated all helium circuits with broadly similar emphasis) with a cryogenic-focus palette. The guiding principle is that colour now encodes temperature: the coldest lines read coolest (deep blue / cyan), the thermal shield reads warm (orange / red) and the warm piping system reads green / olive. This makes the thermal hierarchy of the cryomodule legible at a glance, on A3 and after monochrome plotting.

## 2. New palette

Lines are grouped into three temperature zones. Each primary (main) line has a saturated hue; its branch lines (designator with a prime, e.g. A′) use a darker or lighter shade of the same hue.

### Cold header (top of sheet)

| Line | Designator | Colour | Hex | Service | Temp | Pressure | Flow | DN | MOC |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| A | A | Blue | #0000FF | 4.5 K primary helium | 4.5 K | 3 bar | ~50 g/s | DN50 | SS316L |
| A′ | A′ | Navy | #000080 | 4.5 K branches | 4.5 K | 3 bar | varies | DN25 | SS316L |
| B | B | Cyan | #00FFFF | 2 K primary helium | 2 K | 27 mbar | ~47.5 g/s | DN40 | SS316L |
| B′ | B′ | Teal | #008B8B | 2 K branches | 2 K | 27 mbar | varies | DN25 | SS316L |

### Thermal shield

| Line | Designator | Colour | Hex | Service | Temp | Pressure | Flow | DN | MOC |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| D | D | Orange | #FF8000 | 40 K shield inlet | 40 K | 14 bar | TBD | DN32 | Cu |
| D′ | D′ | Light orange | #FFB366 | 40 K branches | 40 K | 14 bar | varies | DN20 | Cu |
| E | E | Red | #FF0000 | 60 K shield outlet | 60 K | 13 bar | TBD | DN32 | Cu |
| E′ | E′ | Dark red | #CC0000 | 60 K branches | 60 K | 13 bar | varies | DN20 | Cu |

### Warm piping system (WPS) — bottom of sheet

| Line | Designator | Colour | Hex | Service | Temp | Pressure | Flow | DN | MOC |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| W | W | Green | #00FF00 | WPS warm return | 4.5 K → 300 K | 6 bar | ~2.5 g/s | DN20 | SS304 |
| S | S | Lime | #BFFF00 | WPS service / safety | 2 → 292 K | 1.05 bar | TBD | DN15 | SS304 |
| U | U | Olive | #808000 | WPS GHe supply inlet | 292 K | 14 bar | TBD | DN15 | SS304 |

### Reference

| Item | Colour | Hex | Notes |
| --- | --- | --- | --- |
| Outside scope | Grey (dashed) | #808080 | Services beyond the hand-over boundary |
| Secondary / DI-water | Green-blue | per sheet | Cooling water utility |

## 3. Old → new mapping

| Element | v4 (old) | v5 (new) | Rationale |
| --- | --- | --- | --- |
| 4.5 K primary (A) | blue #0000FF | blue #0000FF | retained — coldest reads coolest |
| 2 K primary (B) | cyan #00FFFF | cyan #00FFFF | retained |
| 40 K shield in (D) | red #FF0000 | orange #FF8000 | red re-assigned to the outlet; 40 K reads warm-orange |
| 60 K shield out (E) | (grouped / olive) | red #FF0000 | hottest cryo line gets the hottest hue |
| Warm return (W) | green #00FF00 | green #00FF00 | retained, now anchors the WPS zone |
| Service / safety (S) | — | lime #BFFF00 | new explicit WPS line |
| GHe supply (U) | olive #808000 | olive #808000 | retained |

The key behavioural change: red moved from the 40 K inlet to the 60 K outlet, and the 40 K inlet became orange — so the shield pair D→E now reads as a clear warm-up (orange → red) instead of two reds.

## 4. Branch (prime) shading rule

- Cold lines (A, B): branch = darker shade (A′ navy, B′ teal).

- Thermal lines (D, E): branch = lighter / darker shade of the same hue (D′ light orange, E′ dark red).

- A run is classified primary vs branch automatically using the 55th-percentile run-length threshold per class; primaries live on the main piping layers (04/05/06) and branches on the _BRANCHES layers (04B/05B/06B).

## 5. Where the scheme is applied

- Production sheets — all 16 (QCELL + RFCELL × 2 sheets × STANDARD / CONTROL-CENTRIC × colour / mono).

- Zone bands (layer 02C_Zone_Bands) tint the sheet into cold-header, thermal-shield, equipment and warm-WPS reading zones.

- Line labels (layer 04D_Piping_LINE_LABELS) carry [LINE]-[SIZE]-[MOC].

- Flow arrows (layer 04G_Flow_Arrows) are coloured per line.

- Legend — the on-sheet legend now contains the full line specification table (colour swatch, temperature, pressure, DN, MOC).

- MAIN-LINES-ONLY schematic and the VIEW_MAINLINES_ONLY preset.

## 6. Monochrome behaviour

When colour is removed, the class hierarchy is carried by line weight + dash pattern instead of hue:

| Zone | Mono weight | Dash |
| --- | --- | --- |
| Cold header (A/B) | 1.0 mm primary / 0.6 mm branch | solid |
| Thermal shield (D/E) | 0.8 mm primary / 0.6 mm branch | solid |
| Warm WPS (W/S/U) | 0.5 mm | dashed (8,3) |

This guarantees the drawing survives black-and-white plotting and photocopying without loss of meaning.

## 7. Accessibility / plotting notes

- Blue↔cyan and orange↔red pairs were chosen to remain distinguishable by position (zone bands) even for colour-vision-deficient readers; the mono weight/dash system is the formal fallback.

- All hex values above are the controlled source-of-truth and match generator/line_spec_data.py and LINE_SPECIFICATION_MASTER.xlsx.