# Sensor Re-allocation Mapping

Derived from the QSYS instrumentation-location study (LB / LBI) and the QM instrumentation & controls brainstorming. The goal is to monitor the Piezo (PZ) tuner thermal gradient and the MAG / coupler thermalisation points with the correct cryogenic sensor technology.

## 1. Sensor technologies

| Sensor type | Technology | Best for |
| --- | --- | --- |
| TT-CX | Cernox® resistance thermometer | Coldest points (≤ 4 K range), high sensitivity at low T |
| TT-PT100 | Pt-100 RTD | Warmest points (> 40 K range), stable at higher T |

## 2. Primary re-allocations (PZ — Piezo tuner)

| Original tag | New tag | Sensor type | Position | In source geometry |
| --- | --- | --- | --- | --- |
| TT535 | PZ535 | TT-CX | Coldest part of the Piezo (PZ) | ✅ yes — re-tagged & ring-highlighted on drawing |
| TT525 | PZ525 | TT-PT100 | Warmest part of the Piezo (PZ) | ⚠ design re-allocation — tag not present in current source extract; applied automatically if/when present |

On the drawings, a re-allocated sensor is shown as a normal ISA bubble with a dashed red highlight ring and a red sensor-type label (TT-CX / TT-PT100).

## 3. MAG & coupler-port redistribution

TT-CX and TT-PT100 sensors are redistributed to monitor the MAG component and the coupler thermalisation ports:

| Sensor type | Location | Purpose |
| --- | --- | --- |
| TT-CX | MAG cold port | Cold-end temperature of the MAG |
| TT-PT100 | MAG warm port | Warm-end temperature of the MAG |
| TT-CX | Coupler port (cold) | Coupler thermalisation, cold side |
| TT-PT100 | Coupler port (warm) | Coupler thermalisation, warm side |

## 4. PZ monitoring strategy (summary)

- TT-CX → coldest part of the Piezo (maximum sensitivity in the 2–4 K band).

- TT-PT100 → warmest part of the Piezo (stable readout in the 40–300 K band).

- The pair brackets the PZ thermal gradient so the control system can verify that the actuator stays within its allowable temperature window.

## 5. Where to see it

- Re-allocated PZ sensors appear on the Instrumentation sheets (Sheet 2) of both QCELL and RFCELL, on Layer 9 — Instruments (bubble) with the red highlight, and the sensor-type callout on Layer 12 — Tags.

- The machine-readable record is in _build_meta.json under realloc / mag_coupler.