# MINERVA CryoCell P&ID — Colour & Legend Guide (v4)

Project: MINERVA CryoCell — SCK CEN (MYRRHA/MINERVA Phase 1) Consultant: Mott MacDonald, Bristol UK — MMD 411066 Client: SCK CEN, Boeretang 200, 2400 Mol, Belgium Standard: SCK CEN AD_01.16 (P&ID conventions) Status: S2 — FOR ACCEPTANCE · RESTRICTED

## 1. Purpose

This guide explains the colour coding, line-weight conventions and legend tables used across the v4 MINERVA CryoCell P&ID set. It applies to all four sheets (QCELL =NA.PS01_PFB712 and RFCELL =NA.PS01_PFB713, process + utilities).

The drawing set is designed to be read in two complementary modes:

- Colour (STD) mode — fluid/service class is identified primarily by line colour.

- Mono mode — for black-and-white printing, class is identified by inline pipe names printed directly on the run, plus differentiated line weights and dash patterns. No information is lost when colour is removed.

## 2. Fluid / Service Class Colours

Each process class has a dedicated colour, design temperature and design pressure. These are summarised in the on-sheet Class Legend table (layer 16_Legend).

| Class | Service | Colour | Hex | Design Temp | Design Press |
| --- | --- | --- | --- | --- | --- |
| D | 40 K helium supply | Red | #e00000 | 40 K | 14 bar |
| A | 4.5 K helium | Blue | #0033cc | 4.5 K | 3 bar |
| B | 2 K helium | Cyan | #00a6bd | 2 K | 27 mbar |
| WATER | Cooling water (CW) | Green | #00a000 | Ambient | 4 bar |
| E | 60 K helium shield | Olive | #8a8a00 | 60 K | 13 bar |
| AIR | Instrument / plant air | Magenta | #c000c0 | Ambient | 6 bar (g) |

The colour swatches in the interactive HTML viewer’s layer panel match these hex values exactly, so on-screen toggling reflects the printed legend.

## 3. Mono-Mode Line Weights & Names

When colour is suppressed (mono toggle / black-and-white printing), classes are distinguished by:

- Inline pipe names — the line identifier is printed on the pipe run at regular intervals so the reader never has to trace a line back to a colour key. Examples:

  - 40K PRIMARY (Class D supply header)

  - 2K0-4"-PAC1-BA (Class B, 4-inch, line tag PAC1-BA)

- Line weight — primary process headers are drawn heavier than branch/utility runs.

- Dash pattern — signal and pneumatic lines use distinct dashed/dotted patterns (see Signal Legend below).

This guarantees AD_01.16 legibility on a monochrome A3 plot.

## 4. Signal / Connection Legend

The Signal Legend table (also on layer 16_Legend) documents instrument and connection line styles:

| Line style | Meaning |
| --- | --- |
| Solid heavy | Major process pipe |
| Solid light | Minor process / branch pipe |
| Long dash | Electrical signal |
| Dash-dot | Software / data link |
| Fine dotted | Pneumatic / capillary |
| Double slash break | Pipe class / spec break |

## 5. ISA Instrument Bubbles & Tag Boxes

- Instrument bubbles follow ISA-5.1: circle (field), circle-in-square (DCS/shared), hexagon (computer/PLC), with a horizontal bar for panel-mounted devices.

- Every valve and instrument tag is rendered inside a white tag box so the text stays legible where it overlaps pipes, equipment or hatching — in both colour and mono modes.

## 6. Edge Terminal Points

Off-sheet connections terminate at the drawing frame edge with a cloud-style terminal point carrying the continuation reference (AD_01.10 style). Terminal points are colour-classed in STD mode and labelled with the line name in mono mode.

## 7. Toggling Colour in the Interactive Viewer

In HTML_INTERACTIVE/index.html:

- Mono toggle — switches the whole set between colour and monochrome rendering.

- Style toggle — switches between the filled/coloured presentation and a line-weight-only presentation.

- Layer panel — each class layer has a colour swatch matching the table in §2; toggle individual classes on/off.

See INTERACTIVE_VIEWER_MANUAL.md for full viewer instructions.