# MINERVA CryoCell P&ID v3 — Layer Naming Standard

Project: MINERVA CryoCell — SCK CEN (MYRRHA / MINERVA Phase 1) Standards: ANSI/ISA-5.1-2022 · ISO 10628 · IEC 60617 · SCK CEN AD_01.16

Every v3 SVG uses the same ordered, hierarchical, self-describing Inkscape layer set. Layers are named NN[_Sub]_Category_Detail so they sort correctly and read unambiguously in Inkscape, Illustrator and any SVG editor. Drawing order is bottom (background) to top (annotations).

### Layer table

| # | Layer name | Purpose | Default colour | Line weight |
| --- | --- | --- | --- | --- |
| 00 | 00_Background_TitleBlock | Sheet frame, header strip, compact bottom title block | Black | 0.7–2.0 mm |
| 01 | 01_Scope_Boundaries | AD_01.16 termination-point (TP) scope diamonds | Per category | 1.2 mm |
| 02 | 02_Structure_Reference | Faded reference geometry from source | Grey | 0.5 mm |
| 03 | 03_Equipment_Vessels | Cavities, couplers, HX, vessels, tuners, antennae | Black / brown | 0.5 mm |
| 04A | 04A_Piping_PRIMARY_40K | 40 K shield trunk lines | Red #e00000 | 1.0 mm |
| 04B | 04B_Piping_BRANCHES_40K | 40 K shield branch lines | Red #e00000 | 0.7 mm |
| 05A | 05A_Piping_PRIMARY_4p5K | 4.5 K supply trunk lines | Blue #0033cc | 1.0 mm |
| 05B | 05B_Piping_BRANCHES_4p5K | 4.5 K supply branch lines | Blue #0033cc | 0.7 mm |
| 06A | 06A_Piping_PRIMARY_2K | 2 K return trunk lines | Cyan #00a6bd | 1.0 mm |
| 06B | 06B_Piping_BRANCHES_2K | 2 K return branch lines | Cyan #00a6bd | 0.7 mm |
| 07 | 07_Piping_SECONDARY_Water | DI cooling-water secondary circuit | Green #00a000 | 0.5 mm |
| 08 | 08_Piping_OUTSIDE_SCOPE | 60 K guard / infrastructure / instrument air | Grey dashed | 0.35 mm |
| 09 | 09_Valves_Mechanical | CV/HV/SV/RV/MV/PL valves + bellows | Black | 1.0 mm |
| 10 | 10_Signals_Pneumatic | Pneumatic instrument signals | Purple #7a00a0 | 0.25 mm |
| 11 | 11_Signals_Electric | Electric instrument signals | Blue #00529b | 0.25 mm |
| 12 | 12_Signals_Hydraulic | Hydraulic instrument signals | Amber #a06a00 | 0.25 mm |
| 13 | 13_Instruments_Sensors | ISA instrument bubbles + heat-load markers | Per family | 0.3 mm |
| 14 | 14_Instruments_Control_DIS | DIS interlock, tuner limit switches, Lemo connectors | Black / red | 0.3–1.6 mm |
| 15 | 15_Tags_Instruments | All tag text | Black | — |
| 16 | 16_Legend_TOGGLEABLE | Compact legend overlay (off by default) | Mixed | — |
| 17 | 17_Notes_TOGGLEABLE | Buffer/scope notes and callouts | Green / red | — |

### Piping hierarchy — PRIMARY vs BRANCH

Within each cryogenic class (40 K, 4.5 K, 2 K) the source geometry is split into two sub-layers:

- PRIMARY (…A) — the trunk/header runs, drawn at 1.0 mm.

- BRANCH (…B) — the take-offs and short connections, drawn at 0.7 mm.

The classifier ranks every line segment by its on-sheet length (CTM-resolved). Segments at or above the 55th percentile of their class become PRIMARY; the rest become BRANCH. Junction nodes and coloured fills travel with the PRIMARY layer. Secondary (DI water) is a single 0.5 mm layer; out-of-scope services are a single 0.35 mm grey dashed layer.

### Signal-line differentiation (all 0.25 mm)

To stay legible on monochrome plots each signal type uses a distinct dash pattern, following the intent of AD_01.16 Sheet 1/9:

| Layer | Type | Pattern |
| --- | --- | --- |
| 10 | Pneumatic | long dash + // cross-tick hatch marks |
| 11 | Electric | fine dotted |
| 12 | Hydraulic | dash-dot |

Note on AD_01.16 vs the brief. AD_01.16 represents electrical as dashed, pneumatic with cross-ticks and hydraulic with an “L” mark. The brief asked for pneumatic = dashed, electric = dotted, hydraulic = dash-dot. v3 keeps all three visually distinct and leans on the AD_01.16 cross-tick for pneumatic while using dotted for electric (clearest on A3). The mapping is recorded here and in the on-sheet legend so there is no ambiguity.

### Monochrome (_MONO) variants

Each sheet is also issued as a pure black-and-white _MONO SVG/PDF:

- all piping is black, differentiated only by the weight hierarchy above;

- out-of-scope services stay dashed; signals keep their dash patterns;

- instrument bubbles are white-filled with black outline;

- arrowhead / junction markers are recoloured to black.

### Scope categories (AD_01.16)

Termination-point diamonds carry three compartments: TP / <letter><number> / <next system>. Category letters:

B = Building · C = Civil · E = Electrical · G = Compressed gasses · H = HVAC · L = Liquid waste · S = Solid waste · W = Water