# MINERVA CryoCell P&ID — Reproduction & Standardisation Report

Project: MINERVA CryoCell (SCK CEN / 84836013) Deliverable: Reproduced & improved Piping & Instrumentation Diagrams Standards applied: ISO 10628 (flow diagrams) · ANSI/ISA-5.1 (instrumentation symbols & identification) Sheet format: ISO A3 landscape — 420 mm × 297 mm Version: v2.0 (rebuilt)

## 1. Scope

Two source P&ID sheets were reproduced and improved:

| Key | Source file | Title |
| --- | --- | --- |
| QCELL-LB | PFD-PID MINERVA QCELL-LB.svg | QCELL / LB cryogenic flow scheme (full) |
| RFCELL | PFD-PID MINERVA RFCELL seen by ACR.svg | RFCELL DI-water / coupler module |

The rebuild is data-driven: it re-uses the validated segmentation produced in the previous project stage (segmentation/data/*.json) for all instrument, equipment, safety and vacuum elements, and re-extracts the original process-line geometry with fully resolved transforms so the pipe network is preserved exactly while being recoloured and re-weighted to standard.

### Output files (output/)

| File | Description |
| --- | --- |
| PID_QCELL-LB_improved.svg / .pdf | Improved QCELL-LB sheet (A3) |
| PID_RFCELL_improved.svg / .pdf | Improved RFCELL sheet (A3) |
| TECHNICAL_DOCUMENTATION.md | This report |
| LAYER_STRUCTURE.md | Layer hierarchy reference |
| previews/*.png | Raster previews |

## 2. How the diagrams were rebuilt

The generator lives in generator/:

| Module | Role |
| --- | --- |
| svg_extract.py | Walks the source SVG, accumulates the full CTM for every node, captures every graphic primitive with resolved transform, stroke/fill colour, width, dash and owning layer, and bins it (process line by class, structure, instrument-bubble candidate, dashed boundary, coloured fill/node). |
| symbols.py | ISA-5.1 / ISO-10628 symbol primitives: instrument bubbles, valves (manual / control / solenoid / relief), vessels, cavity/coupler bodies, heat exchangers, terminal points, heat-load callouts, junction nodes. |
| build_pid.py | Composes the A3 sheet: frame + title block, equipment, colour-segmented process lines, vacuum barriers, fresh ISA instrument bubbles, ISA tags and the full legend. Emits SVG and feeds the PDF conversion. |

Re-run with:

cd generator && python3 build_pid.py

## 3. Improvements made

### 3.1 Sheet, border & title block

- Re-laid out on a true ISO A3 landscape canvas (420 × 297 mm, viewBox 0 0 1587.273 1122.430, ratio 1.41414).

- Added a double-line drawing border and a structured title block (project, title, drawing number, standard, revision).

- The original drawing content is mapped uniformly into a reserved content region so the border, the right-hand legend column and the bottom class-legend band never overlap the schematic.

### 3.2 Layer hierarchy (ISO logical structure)

The drawing is organised into the requested 7-level Inkscape layer hierarchy with process lines split into colour/class sub-layers — see LAYER_STRUCTURE.md.

### 3.3 ISA-5.1 instrumentation

- Every field instrument is redrawn as a standard circular bubble with a two-line tag (measured-variable + function letters over loop number), e.g. TT / 514.

- Tag grammar follows ISA-5.1: first letter = measured variable, succeeding letters = function:

  - T Temperature, P Pressure, L Level, F Flow, E Electrical, A Analysis, S Speed/Safety, R Radiation …

  - T Transmitter, I Indicator, S Switch, V Valve, E Element …

  - Examples present: TT temperature transmitter, PT pressure transmitter, LT level transmitter, FT flow transmitter, LS level switch, EH electric heater, PZ/FZ safety variants, AP analysis/antenna probe.

- Bubble fill encodes the instrument family (per the source legend): white = LB cryo instrument, salmon = RFCELL instrument, light-blue = LBI-specific instrument.

- Protection / safety instruments (SV, RV, PL, PZ, FZ …) use a dashed bubble outline — the ISA convention for interlock/safety functions.

- Valves are drawn with correct bodies and actuators: hand valve (hand-wheel), control valve (diaphragm), solenoid valve (S box), relief valve (angle/spring) — replacing generic bubbles for HV/CV/SV/RV.

### 3.4 Colour segmentation of process lines

The original used inconsistent / very light screen colours. Lines are now recoloured to a consistent, print-legible palette, one Inkscape sub-layer per class, with standard weights and line styles:

| Class | Service | Colour | Line style |
| --- | --- | --- | --- |
| A | 4.5 K / 3 bar — LHe supply | blue #0033cc | solid, heavy |
| B | 3.5 K / 27 mbar — 2 K LP return | teal #00a6bd | solid, heavy |
| D | 40 K / 14 bar — thermal shield | red #e00000 | solid, heavy |
| E | 60 K / 13 bar — return / He-guard | olive #8a8a00 | solid, heavy |
| Water | DI cooling water (coupler / FREIA) | green #00a000 | solid, medium |
| QINFRA | infrastructure scope division | dark green #006400 | dashed |
| Inst. air | pneumatic 6 (5–7) bar(g) | magenta #c000c0 | dash-dot |

Bulky solid colour blocks in the source were converted to translucent service zones (22 % fill) so they read as highlighting rather than obscuring the schematic; pipe junctions are drawn as small solid nodes in the class colour.

### 3.5 Vacuum barriers & boundaries

Dashed structural boundaries (vacuum vessel / scope divisions) are collected into a dedicated L4 — Vacuum Barriers & Boundaries layer with a standard dashed style, plus the explicit “vacuum barrier” annotation.

### 3.6 Legend enhancement

A comprehensive two-part legend was added: - Right column: instrument-bubble key (families + safety), tag-grammar note, valve & equipment symbols, heat-load callout, terminal/scope point, vacuum boundary. - Bottom band: process-line class legend mapping each colour to its temperature/pressure service and description.

### 3.7 Quality

- Standardised line weights and rounded joins/caps.

- Minimum on-sheet text sizes kept legible (≈ 6 pt and up).

- Suppressed the messy/overlapping original bubble circles and redrew clean ones.

- Markers (arrowheads) and gradient/def references from the source are carried over so flow-direction arrows are preserved.

## 4. Element inventory (from segmentation)

| Metric | QCELL-LB | RFCELL |
| --- | --- | --- |
| Instrument tags | 230 (221 unique) | 67 (45 unique) |
| Equipment items | 42 | 2 |
| Safety devices | 13 | 6 |
| Vacuum barriers | 5 | 0 |
| Temperature points | 77 | 23 |
| Pressure points | 28 | 11 |
| Process-line classes | A,B,D,E,Water,QINFRA,Air | A,B,D,E,Water,QINFRA,Air |

Instrument prefixes encountered (ISA-5.1): TT, TE, PT, PI, PZ, LT, LS, LI, FT, FI, FZ, EH, SM, RS, AP, AA, AD, ED, CV, HV, SV, RV, PL, KW, AK, MV, HL, HX, CF.

## 5. Limitations & notes

- The source sheets are intentionally very dense; the rebuild preserves the real topology and instrument positions rather than re-routing pipes, so localised crowding inherent to the originals remains.

- Colour-to-class mapping is taken from the drawing legend; a few low-confidence source colours (grey shading, near-black) are treated as structure.

- Geometry fidelity is exact (transforms are baked); symbology and styling are the standardised improvement layer.