# Phase 1 — Reference P&ID Analysis (AD_01.10 / 11 / 14 / 17)

Extracted best-practice conventions from the SCK CEN / Mott MacDonald example drawings to drive the v4 refinement.

## Source drawings reviewed

| Drawing | Content | Size |
| --- | --- | --- |
| AD_01.10 P&ID PCW (TP2=PS01.PAB12) | Process Cooling Water P&ID (2 sheets: notes + diagram) | A4/A3 |
| AD_01.11 P&ID Instrument Air (TP2=PS01.QFB10) | Instrument-air P&ID (3 sheets) | A4/A3 |
| AD_01.14 Piping Layout - Instrument Air (PS05.QFB10) | Piping GA / layout | A3 |
| AD_01.17 Instrument Air - Piping Routing & Layout | Routing layout | A0 |

## 1. Terminal-point (TP) placement — KEY FINDING

Terminal points sit at the left and right page edges (and occasionally top/bottom for vertical flows). Each TP is a small assembly, not a bare diamond:

┌───────────────────────────┐  ← scalloped "cloud" callout
   │        WATER GLYCOL        │     · system / medium name (top line)
   │  ◁ =NP.PS01_PFB503 │ 7884 │     · arrow box: destination DWG ref + line no.
   │   FROM MAC (WEST GALLERY) │     · TO/FROM <area> annotation (bottom line)
   └───────────────────────────┘
              ◇ TP.PS01.4002          ← TP diamond w/ TP code + category flag (△B) + NOTE ref
              │
        ──────┘ (pipe continues into / out of the drawing)

- Arrow direction encodes flow: left-pointing arrow = incoming (FROM), right-pointing = outgoing (TO).

- The pipe runs to the frame border with a short connection stub.

- “FROM SHEET 2 / TO SHEET 2” clouds appear at the bottom edge for inter-sheet continuation.

- Each TP carries a category triangle (△B etc.) and a NOTE n reference.

## 2. Line naming strategy

Lines are labelled inline, sitting on the pipe in a small white gap: BR0021-4"-PAC1-BA = line-number – size – fluid/spec-class – insulation/route code. Labels repeat along long runs and at every branch. This is the mechanism the reference uses to keep a monochrome drawing readable — the name on the line, not colour, is the primary identifier.

## 3. White boxes for tags

Every instrument / valve tag (e.g. AA0019, AA3001 / MOV-03) sits in a small white rectangle so it never collides with piping behind it. Tag boxes are opaque white with a hairline border and live on the topmost layer.

## 4. Valve orientation

- Valves are drawn in-line with the pipe (gate-valve bow-tie), white-filled with a black outline so they read clearly where they cross a coloured/black line.

- Actuated valves (MOV, control) add the actuator glyph above the body.

- Tags are placed in white boxes directly below the valve.

## 5. Other conventions adopted

- Scalloped “cloud” callouts for off-sheet/area references.

- Category triangles (△B/C/E/…) used as note + scope flags.

- Reference-drawings list and a “Key to symbols” cell in the title strip.

- Branch take-offs carry their own line number.

## How v4 applies these

| Reference convention | v4 implementation |
| --- | --- |
| TP at L/R edges with cloud + diamond + arrow | terminal_point_edge() on layer 02_TerminalPoints_EDGE; stacked along frame edges |
| Inline line names (mono legibility) | new layer 04C_Piping_LINENAMES + line_label() |
| White tag boxes | tag_with_box(); instrument/valve tags on 12_Tags_Instruments (front) |
| In-line + control-view valves | primary in-line valves + 08B_Valves_HORIZONTAL_OVERLAY tracked-asset row |
| Flow-direction arrows | arrow heads in TP assemblies (TO/FROM) |